Owner’s Manual

INCLUDES

User, Maintenance, Service, and Installation Instructions



**890 BF**



Keep this booklet for service log and future reference

IMPORTANT





For use in Great Britain and Ireland.

**Literature NO 6541 (ISS 12)**

Contents

[EXTENDED FIVE YEAR PARTS WARRANTY 2](#_Toc444761067)

[Benchmark Scheme 3](#_Toc444761068)

[**SECTION ONE Important Information (user instructions)** 5](#_Toc444761069)

[**SECTION TWO Introduction (user instructions)** 7](#_Toc444761070)

[**SECTION THREE Operation (user instructions)** 7](#_Toc444761071)

[**SECTION FOUR Cleaning & Laying the fuel bed (users instructions)** 11](#_Toc444761072)

[**SECTION FIVE Appliance Data (installation instructions)** 17](#_Toc444761073)

[**SECTION SIX Regulations and Warnings (installation instructions)** 18](#_Toc444761074)

[**SECTION SEVEN Siting the Appliance (installation instructions)** 19](#_Toc444761075)

[**SECTION EIGHT Preparing the Appliance for Installation (installation instructions)** 20](#_Toc444761076)

[**SECTION NINE To Install the Appliance (installation instructions)** 21](#_Toc444761077)

[**SECTION TEN CONNECTING THE GAS SUPPLY (installation instructions)** 23](#_Toc444761078)

[**SECTION TEN Assemble the Appliance (installation instructions)** 25](#_Toc444761079)

[**SECTION ELEVEN Check Operation of Fire (installation instructions)** 25](#_Toc444761080)

[**SECTION TWELVE Instruct and Advise the Customer (installation instructions)** 26](#_Toc444761081)

[**SECTION THIRTEEN Maintenance Instructions (maintenance instructions)** 27](#_Toc444761082)

[**SECTION THIRTEEN Wiring Diagram (maintenance instructions)** 29](#_Toc444761083)

[BALANCED FLUE GAS FIRE COMMISSIONING CHECKLIST 30](#_Toc444761084)

[SERVICE RECORD 31](#_Toc444761085)



# EXTENDED FIVE YEAR PARTS WARRANTY

**In order to validate your extended 5 years parts warranty please read the Benchmark Scheme on the opposite page and ensure your installer has filled in the appropriate checklist.**

**This in no way reduces your statutory rights**

Your warranty commences from the date of purchase and you must retain your receipt or invoice as proof of a purchase date.


THIS EXTENDED WARRANTY SPECIFICALLY EXCLUDES GLASS AND SOFT REFRACTORY COMPONENTS, THE BULB AND ANY BATTERIES.

Terms and Conditions

1. The appliance must be installed by a GAS SAFE registered person.
2. The appliance must be used in accordance with the user’s instructions.
3. The appliance must be serviced annually by a GAS SAFE registered person.
4. The benchmark and service log must be correctly filled out and the record of annual services must be up to date and supported by receipts in each case.
5. This warranty is not transferable and relates to the original installation only.
6. The appliance has not been subjected to misuse or accident or been modified or repaired by any person other than the authorised employee or authorised representative of Charlton and Jenrick Ltd.
7. The registration form must be returned within 1 month of purchase.

**Technical Help Desk 01952 200 444**

# Benchmark Scheme



Charlton and Jenrick Ltd is a licensed member of the Benchmark Scheme which aims to improve the standards of installation and commissioning of domestic heating and hot water systems in the UK and to encourage regular servicing to optimise safety, efficiency and performance. Benchmark is managed and promoted by the Heating and Hotwater Industry Council. For more information and the full code of practice please visit [www.centralheating.co.uk](http://www.centralheating.co.uk)

Please ensure that the installer has fully completed the Benchmark Checklist on the inside back pages of the installation instructions supplied with the product and that you have signed it to say that you have received a full and clear explanation of its operation. The installer is legally required to complete a commissioning checklist as a means of complying with the appropriate Building Regulations (England and Wales).

All installations must be notified to Local Area Building Control either directly or through a Competent Persons Scheme. A Building Regulations Compliance Certificate will then be issued to the customer who should, on receipt, write the Notification Number on the Benchmark Checklist.

This product should be serviced regularly to optimise its safety, efficiency and performance. The service engineer should complete the relevant Service Record on the Benchmark Checklist after each service.

The Benchmark Checklist will be required in the event of any warranty.

It is a requirement that the gas fire is installed and commissioned to the manufacturer’s instructions and the data fields on the commissioning checklist completed in full.

To instigate the guarantee, the gas fire needs to be registered with the manufacturer within one month of the installation.

To maintain the guarantee, it is essential that the gas fire is serviced annually by a Gas Safe registered engineer. The service details should be recorded on the Benchmark Service Interval Record and left with the householder.

**Important**

For future reference we suggest you record the following details here, and keep the receipt as proof of purchase. This information may be asked for when you contact the helpdesk.

|  |  |  |  |
| --- | --- | --- | --- |
| **MODEL:** | **INFINITY 890 BF** | **Serial No.** |  |

This information can be found on the label attached to the packaging and on the data badge, which is located on the base of the appliance behind the control cover.

|  |  |
| --- | --- |
| **Retailer Name:** |  |
| **Address:** |  |
|  | |
| **Date Of Purchase:** |  |

**Register your appliance online today to activate your warranty**



# **SECTION ONE Important Information (user instructions)**

**Consumer protection information**

As manufacturers and suppliers of heating products, we take every care, as far as is reasonably practicable, that these products are so designed and constructed as to meet the general safety requirement when properly used and installed. To this end, our products are thoroughly tested and examined before despatch.

**IMPORTANT NOTICE:** Any alteration that is not approved by the appliance manufacturer could invalidate the approval of the appliance, operation of the warranty and could affect your statutory rights.

**Health and safety notice**

**Important**

This appliance could contain some of the materials, indicated below, that could be interpreted as being injurious to health and safety. It is the users / installers responsibility to ensure that the necessary personal protective clothing is worn when handling these materials, see below for information.

**Artificial Fuels, Mineral Wool, Insulation Material, Refractory/Ceramic Fibres, Glass Yarn -** *may be harmful if inhaled, may be irritating to skin, eyes, nose and throat.*

**When handling** *avoid inhaling and contact with skin or eyes. Use disposable gloves, facemasks and eye protection. After handling wash hands and other exposed parts. If a vacuum is used for cleaning the coals or cleaning after servicing / installation it is recommended that it be of the type fitted with a HEPA filter.*

**Disposal of refractory/ceramic materials**. *To keep dust to a minimum these materials should be securely wrapped in polythene and be clearly labelled ‘RCF waste’. These materials are not classified as ‘hazardous waste’ and should be disposed of at a site licensed for the disposal of industrial waste.*

**INTRODUCTION**

* The INFINITY 890 BF is an inset room sealed decorative fuel-effect gas appliance.
* The INFINITY 890 BF is available in **Natural Gas only and L.P.G**
* The INFINITY 890 BF **must not** be installed into a natural draught flue or chimney.
* The INFINITY 890 BF should only be installed and serviced by a competent person i.e. GAS SAFE registered, in accordance with the GAS SAFETY (INSTALLATION AND USE) REGULATIONS.
* The INFINITY 890 BF does not require a chimney, but **must be** installed against an outside wall.
* It is important that the flue terminal is regularly checked and kept clear at all times.
* If the terminal is accessible to people (i.e. less than 2m above a walkway, balcony etc.) the terminal guard must be fitted to prevent access to the flue outlet, which becomes hot when the fire is in use.
* As the INFINITY 890 BF is a room sealed appliance (i.e. air for the combustion process is taken from outside the room) no purpose built ventilation is required.
* The INFINITY 890 BF is designed and tested to meet the requirements of the European Standard EN 613.
* The Appliance is for use on Natural Gas ( G20 @ 20mbar ) & L.P.G ( G31 @ 37mbar )
* Failure to install appliance correctly could lead to prosecution.

**In GB (Great Britain),** the appliance must be installed by a competent person i.e. GAS SAFE registered, in accordance with the GAS SAFETY (INSTALLATION AND USE) REGULATIONS, The Building Regulations (or The Building Regulations (Scotland) or The Building Regulations (Northern Ireland)) and The Current I.E.E. Wiring Regulations, if appropriate.


**In IE (Ireland),** the appliance must be installed by a competent person and installed in accordance with the current edition of I.S.813 Domestic Gas Installation, the current Building Regulations and the current ETCI rules for electrical installation, if appropriate.

* Although the INFINITY 890 BF is fitted with a glass front which acts as a dress guard it is strongly recommended that a fireguard should be used for the protection of children, the elderly or infirm. Fireguards should conform to B. S. 6539 (1984) (Fireguards for use with solid fuel appliance).
* Care should be taken to prevent any damage being caused to surrounding soft furnishings or decoration. Many wall coverings may become discoloured if placed too close to the appliance, it is strongly recommended that any proposed wall covering intended for use immediately above the appliance should be tested in the hottest position (immediately above) first. Run the fire on high over a few days
* All combustible material must be removed from behind the fire and fire trim.
* The first time you light your new appliance a smell may occur due to its new condition. This is quite normal and will soon disappear after a few hours use at maximum setting (open a window until the smell disappears)
* With use the inside of the air box will change colour, particularly the sides and rear. This is quite normal and often adds to the overall effects of the appliance.
* The appliance **MUST NOT** be used if the glass panel is not correctly fitted or if this panel is cracked or broken.
* Any debris should be cleaned from the appliance. A vacuum cleaner can be used but only after all the loose shapes have been removed.
* ***Prior to removing or cleaning the fuel bed refer to the ‘Health and Safety Notice’ located on page 3 of this booklet***.
* The appliance should be serviced annually by a competent person i.e. a **GAS SAFE registered engineer** in accordance with these instructions.
* The glass or any part of the appliance **MUST NOT** be cleaned or wiped whilst the appliance is **HOT**, to do so could be dangerous and may damage the paintwork of the appliance.

# **SECTION TWO Introduction (user instructions)**

* The INFINITY 890 BF is an inset room sealed decorative fuel-effect gas appliance designed for use in locations that do not have a conventional chimney. The appliance must be installed against an outside wall because the air to support combustion is taken from the outside and the products of combustion are expelled to the outside.
* The appliance incorporates a safety device in the form of a FLAME SUPERVISION DEVICE, which constantly monitors the flame and will cause the gas to be switched off if the flames are extinguished for any reason. **THIS DEVICE MUST NOT BE OVERRIDDEN.** If this situation occurs on a regular basis have the appliance checked by a qualified engineer. The problem may be due to a blocked or restricted flue.
* Before removing the, trim, glass shapes for cleaning the fire should be turned off, and left to cool down.
* **NOTE:** In use some discoloration of the components will take place in the combustion box, this is normal, but can be kept to a minimum if the shapes are placed correctly (i.e. after cleaning). See Section 4.
* As with all heating appliances certain areas (Working Surfaces) become very hot when the appliance is in use.

# **SECTION THREE Operation (user instructions)**




**Display overview**

Press  to awaken the handset from its dormant sleep mode at any time. Fig 1 shows the display neutral, ready to turn on.

**Turn on (start up).**

Pressing and holding  displays an “UNLOCK” graphic Fig 2 prompting the  button to be pressed simultaneously. Whilst both  &  are pressed a progress bar Fig 3 will complete. If either button is released before the progress bar has completed the operation will cancel. Once the progress bar has completed the handset will display the status of the fire (priming – ignition – pilot – main burner) finishing at the fire “on” display screen Fig 4.



**Flame height adjustment**

Once the fire has been started the flame height can be decreased by moving your finger clock wise or decreased moving your finger anti-clock wise using the selector wheel. Once the desired flame level is set, remove your finger from the selector wheel to transmit your selection to the receiver. Six flame levels and a pilot setting are selectable. Press whilst the display is active to display the current flame level.

**Turn off (shut down)**

To turn the appliance off, press and hold down until the progress bar has completed. If the is released before the progress bar has completed the operation will cancel.

**Mode select**

With the fire running on manual operation you can access three further “modes”. Press for “mode”. Use the selection wheel to cycle through the three options, “Auto”, “Sleep” and “Light”. Press to select “Auto” or “Sleep”

Sleep:- Use the selector wheel to choose from the available time range of 5 minutes to 1 hour 30 minutes. Once the desired countdown time has expired the appliance will turn off. By pressing the button during the countdown will cancel the countdown timer if required.


Note: The handset contains a sensitive temperature measurement device. To achieve the best thermostatic efficiency do not place the handset near the heat source, avoid covering, direct sunlight or near a draft or open window etc. Place the handset at a midpoint in the room or area being heated. Allow 5-10 minutes for the handset to stabilize if subjected to extremes of temperature.

**Auto (Thermostatic) Control**

Press to awaken the handset from its dormant sleep mode at any time.

**Selecting auto control**

The “auto” function can only be selected once the appliances has been started and initiated into “manual” mode. Once in manual mode, press and release the  button to enter the “mode” options. Auto is the first option, press to enter auto mode.

****

**Adjusting target temperature**

Use the selection wheel to increase or decrease the temperature to the desired level, release your finger from the wheel to transmit the target temperature (See Fig 5) to the receiver. The “auto” function will now modulate the flame height to achieve your target temperature. The selectable temperature range is 1 degree C to 29 degree C.

**Cancelling auto function**

Press  to “end” and cancel the “auto” control. The handset will return to manual control.

**Menu features**

The menu can be accessed by pressing and holding the button (approx. 5 seconds) until the menu graphic completes (see fig 6). Use the selector wheel to highlight one of the available options. Press to enter the required option.

**Set clock**

The handset clock has a dedicated 24 hour display. Use the selector wheel to firstly set the hours. Press to change to minutes select. Use the selector wheel to change the minutes. Press the button to alternate hours and minutes to make any other alterations. Finally, press the button to save the clock setting.

**Display**

Temperature display units-use selector wheel to select either Celsius (degree C) or Fahrenheit (degree F). Press the button to save selection.

**Gas fire (pair code)**

The device screen displays the current operating channel of the handset. To delete the channel press & simultaneously or to return to the menu option.

**Reset**

To restore the handset back to its original factory setting select “reset” from the menu options. Press - & - simultaneously to complete the reset command – to return to the menu options.

**Changing The Handset Batteries.**

The handset operates from four AAA 1.5V batteries. New alkaline batteries are recommended. Do not mix new and old batteries. When inserting the batteries, observe and position batteries according to the battery compartment graphics (see Fig 7). When the batteries are inserted this handset will attempt to repair.



**\*Important : If the fire burner or pilot is extinguished for any reason, do not attempt to re-light the pilot for at least 3 minutes.**

# **SECTION FOUR Cleaning & Laying the fuel bed (users instructions)**

**CLEANING: DECORATIVE FASCIA**

* Fascia assembly can be wiped with a soft, clean, dry, cloth only.

**CLEANING: BLACK PAINTED SURFACES**

* These surfaces should be dusted regularly and any marks removed with a soft cloth.
* Abrasive or chemical cleaner should never be used.

**CLEANING: GLASS PANEL**

From time to time it may be necessary to clean the glass panel.

We recommend you use a Ceramic Hob Cleaner (brands such as **HOB BRITE and VITRO CLEN have been found to be acceptable)** these are available from most leading Supermarkets.

Remove the glass panel as follows:

* Undo the 3 screws that secure the heat deflector and remove
* Carefully lift off the outer fascia held in place by magnets.
* Remove the 4 nuts at the bottom securing the glass assembly.
* Remove the Top 5 castle nuts on Glass Clamp, and slide the Glass Frame & Retaining Bracket completely off and disengage both parts
* Lay the glass panel down on a flat working surface on top of an old opened newspaper with the side to be cleaned uppermost.

**Follow the Instructions on the Hob Cleaner Bottle.**

On stubborn stains (where the appliance has been used for a long period without glass panel being cleaned), use a new **Brillo Pad** well wettedwith the Hob cleaner applied directly to it.

Ensure all the residues of the cleaner are removed with a damp cloth and the glass panel is completely dry before fitting to the appliance.

Note: - If the loose shapes have not been placed correctly, causing the gas flame to contact the glass this may result in glass staining that cannot be removed by cleaning.

* Re-assemble in reverse order ensuring a tight seal against glass assembly.
* Re-fit the fascia.

**CLEANING AND REPLACING fuel bed shapes**


**Important: - Refer to the ‘Health & Safety Notice located on page 3 of this booklet before cleaning or replacing any refractory material.**

**Use only the shapes provided NO OTHER SHAPES SHOULD BE ADDED to the appliance**

**The Fuel bed set consists of:**

* Log fuel bed complete set consisting of :-
* 11 Log Shapes. ( 9 x large shapes & 2 x small shapes. )
* 1 Bag of Bark Chips.

**Log Fuel Bed Layout.**

****

* The Burner End Plates should already be in position at ends of burner carrier and held in place with two self tapping screws with the chamfered ends towards the front.
* The Air Bridge should already be fitted at the rear and held in place with two M4 x 10mm screws at either end.
* Place to Burner Bar Edge Cover over the front of the Burner Bar with the slot at the left hand side so it covers the edge.



* Place a single layer of Bark Chips on the front of the burner and the outside of the Burner End Plates, making sure they don’t go over the Burner Channel, the Pilot cross lighting ports on the right hand side of the burner or the pilot assembly.
* **AVIOD PLACING BARK CHIPS OVER BURNER SLOT ON BURNER BAR.**
* **AVOID BLOCKING PILOT ASSEMBLEY.**



* Place the first three rear straight log shapes on top of the Air Bridge as far back to the rear as possible as shown in the picture and space them evenly.



* Place the next Two large shapes and One small shape as shown making sure they do not move the bark chips so that they cover the burner channel, the smallest log shape goes in the left corner on top of the bark chips on the Burner End Plate for decorative effect.



* Position the Smallest Log shape as shown in picture.



* Place the next Two Middle shapes as shown, resting on the rear shapes, making sure they do not disturb the Bark Chips or move them into the Burner Channel.



* Place the last two large shapes and last small shape as shown, making sure the last right hand shape does not cover the pilot flame. The last small shape goes across the Burner and the Burner End Plate as far forward as possible to keep it out of the pilot flame as much as possible. (the small shape is for decorative effect ).



* When positioning the Small Log Shape, make sure as not to place it over the pilot assembly as this will disturb the pilot flame, please see picture

# **SECTION FIVE Appliance Data (installation instructions)**

Fire Box dimensions: Height 456mm

Width 970mm

Forward Projection: 10mm

Overall Trim dimensions……………………………………………….Height 462mm

Width 1054mm

Trim Forward dimensions…………………………………………… 23mm

Weight: 35kg

Flue Length…………………………………………………………………..100mm (minimum) to 1000mm (maximum)

Standard length supplied with fire 535mm (267.5mm after cutting). Additional 535mm or 1000mm tubes supplied as optional extras. (No bends or joined flue pipes should be used in the flue system).

Pressure Test Point Location: Gas inlet elbow

Gas Connection: 8.0mm O/D, tube.

Data Badge Location: On bottom right hand side of firebox under batteries.

|  |  |  |
| --- | --- | --- |
| **MODEL** | **Natural Gas (G20) Version** | **L.P.G (G31) Version** |
| Category of appliance | CII | CII |
| NOX Class | 5 | 5 |
| Efficiency Class | 1 | 1 |
| Gas Category | I2H | I3P |
| Gas Type | G20 Natural Gas | G31 L.P.G |
| Gas Pressure +/- 1.0mbar | 20 mbar | 37 mbar |
| Gas Input (Max) | 3.4 KW Gross | 3.2 KW Gross |
| (Min) | 1.6 kW Gross | 1.6 KW Gross |
| Injectors size | 230 Mark | 300 Mark |
| Handset Replacement Batteries 4 x AAA 1.5V | | |
| Power Supply Type Plug – Input : 100-240 VAC 50/60 Hz, 0.2A | | |

NOTE: The efficiency of this appliance has been measured as specified in BS EN613-2001 and the result is 82.1% natural gas & L.P.G. The gross calorific value of the fuel has been used for this efficiency calculation. Gastec have certified the test data from which it has been calculated. The efficiency value may be used in the UK Government’s Standard Assessment Procedure (SAP) for energy rating of dwellings.

# **SECTION SIX Regulations and Warnings (installation instructions)**

* This appliance must only be installed in Great Britain or Ireland.
* The appliance is available in natural gas and L.P.G.
* This appliance must be installed on a suitable outside wall.
* No special ventilation bricks or vents are required into the room containing the appliance.
* **In GB (Great Britain)**

It is the law that all gas appliances must be installed by a competent person; i.e. a GAS SAFE registered installer, in accordance with the current Gas Safety (Installation and Use) Regulations (as amended), all relevant parts of the local and national building regulations and all relevant recommendations of the current British Standards. Failure to do so could lead to prosecution.

The following are the relevant codes of practice and British Standards: -

B.S. 5871 PART 2 B.S. 5440 PART 1

B.S. 6891 B.S. 1945

Note:- This appliance must be installed to current versions of the above standards and include any relevant amendments.

The Building Regulations issued by The Department of the Environment.

The Building Standards (Scotland) (Consolidated) Regulations issued by The Scottish Development Office.

* ***IN IE, (Ireland)***

The appliance must be installed by a competent person and installed in accordance with the current edition of I.S.813 Domestic Gas Installation, the current building regulations, and the current ETCI rules for electrical installation, if appropriate.

**WARNINGS**


* As this appliance has components, which get very hot as with all such fires, it is recommended that a fireguard should be used for the protection of children, the elderly, or the infirm. Fireguards should conform to B.S.6539 (1984) (Fireguards for use with solid fuel appliances).
* During initial use, an odour may be evident. This will soon disappear if the fire is run on its maximum setting for a few hours.
* Care must be taken to prevent any damage being caused to surrounding soft furnishing or decoration, e.g. wall coverings may become discoloured if placed too close to the appliance.

# **SECTION SEVEN Siting the Appliance (installation instructions)**

(When installing in a timber framed dwelling reference must be made to the specific installation requirements stated in **Section 9 Installing the Appliance in Timber Framed Dwelling**).

**GENERAL REQUIREMENTS**

* The flue and air duct length must be between 100mm to 1000mm.
* The fire is supplied with a standard pipe length of 535mm (to be cut in half to make a flue duct and air duct length of 267.5mm.) The 535mm length of flue can be cut down as required.
* The flue and air duct must not have any bends.
* The flue outlet must terminate on a suitable outside wall.
* The minimum flue terminal clearances, which must be maintained, are as shown below.



1. Directly below an openable window or other opening. E.g. air brick 300mm
2. Below gutters, soil pipes or drain pipes 300mm
3. Below eaves 300mm
4. Below balconies or carport roofs 600mm
5. From vertical drain pipes and soil pipes 75mm
6. From internal and external corners 300mm
7. Above ground, roof or balcony level 370mm
8. From a surface facing the terminal 600mm
9. From a terminal facing the terminal 1200mm
10. From an opening in a car port into a dwelling e.g. door, window, etc 1200mm
11. Vertically from a terminal on the same wall 1500mm
12. Horizontally from a terminal on the same wall 300mm

**\*To minimise the risk of cracking, due to heat expansion, the use of marble slips is recommended\***

* The back panel of the surround must have a cutout within the maximum and minimum dimensions as shown.

ALL DIMENSIONS IN mm

#### B

##### “A”

HEARTH TO SHELF

430 MIN-

445 MAX.

900 MIN

935 MAX.

170 MIN.

* Ensure that gas supply is suitably sited.
* The appliance may be fitted without a hearth (Hole in the Wall type installations), 150mm min. from the floor to the base of appliance.
* The minimum clearance from the hearth (base of appliance) to the underside of a combustible shelf should be determined using the shelf chart.
* Check with the supplier or manufacturer that the surround meets 1500C minimum rating (attention should especially be given to man-made materials such as resin).

**\*Please note - Appropriate measures should be taken when installing into a working flue system i.e. out through an existing chimney \***


# **SECTION EIGHT Preparing the Appliance for Installation (installation instructions)**

* Carefully unpack the appliance from the carton and check the contents.
* Lift away the Box of ceramics, glass panel and trim.
* Remove the refractory components from the inside of the packaging.
* Remove the glass panel and air bridge from the packaging.
* The appliance is now ready for installation.

# **SECTION NINE To Install the Appliance (installation instructions)**

**INSTALLING THE APPLIANCE INTO CAVITY WALL.**

* Ensure it is a suitable outside wall constructed of non-combustible materials and that the flue position meets the requirements previously described in **Section 8**.
* Mark a horizontal line on the wall at the intended appliance base height 150mm min from combustible surface or 50mm min from non-combustible hearth.
* Mark a vertical line on the wall at the intended centre of the appliance up from the horizontal line for a height of 430mm.
* If insetting into the wall mark the position for a lintel above the top horizontal line.
* Mark a short horizontal line so it crosses the centre line at 75mm above hearth level line. This is the centre point for the Air Duct pipe hole.
* Mark a short horizontal line so it crosses the centre line at 355mm above hearth level line. This is the centre point for the Flue Duct pipe hole.
* Using a long masonry drill, make two pilot holes completely through the wall. Ensure the holes are drilled accurately at the centres and square to the wall both horizontally and vertically at the cross points previously marked.
* If insetting into the wall proceed as follows: Cut out the brickwork of the inner skin of the cavity wall for the lintel, and fix the lintel.
* Cut out the brickwork under the lintel, between the two outside vertical lines into the cavity. Ensure the cut out width is square and try the appliance into the opening.



* Using 125mm (5”) core drill cut two holes following the pilot holes. Drill from the outside through to the cavity to give a good finish on the outside.
* Remove any cavity insulation from the cut out opening and for a further 100mm into the cavity gap each side and above.
* Pack “Rockwool” around the sides and top of the opening into the cavity for a depth of 100mm. Also put some behind the firebox if space is available.
* Lay the hearth if required so that it is positioned correctly to the horizontal line.
* Offer the appliance into the opening and mark through the gas pipe entry hole (see connecting the gas supply section).
* Pass a tape measure through the core-drilled holes and record the distance from the spigots to the surface of the outside wall. Include the length of the spigots themselves in this measurement and increase both the recorded distances by 15mm (5/8”) each for the engagement allowance.
* Cut the lengths from the one 535mm flue pipe provided, if the length is longer than 267.5mm you will require an extra flue pipe.(535mm standard or 1000mm optional)
* Remove the appliance from the opening, and position the gas supply (see connecting the gas supply later in this manual), taking account of the relative gas regulations regarding a gas pipe in a cavity (sleeving and sealing etc). Note the gas feed must be fitted with an isolation valve.
* Position and seal the pipes to their respective spigots on the rear of the appliance (use flue seal or fire cement to ensure airtight seal, it must not obstruct the flue).
* Peal the backing off the length of foam seal and affix to the rear outer edge of the appliance flange.
* Push the appliance back into the opening and fill any space behind the appliance with “Rockwool”.
* Complete the gas connection (see connecting the gas supply later in this manual).
* Drill the four fixing holes through the hole in the flange of the appliance and fix back using plug and screws.
* Fit the outer wall terminal plate, with the “Rockwool” gasket sandwiched between it and the wall, with the double spigot at the top so that it seals to both the flue pipe and the air duct, (use flue seal or fire cement to ensure air tight seal, it must not obstruct the flue).
* Drill through the four holes in the outer wall terminal plate and fix back to the wall using plugs and screws.
* Position the outer terminal cover and fix to wall terminal plate with the four screws provided.
* If the flue outlet is fitted below 2m from the floor or a balcony then a flue terminal guard must be fitted.

# 

# **SECTION TEN CONNECTING THE GAS SUPPLY (installation instructions)**

**TURN OFF ANY GAS APPLIANCES THAT ARE FED BY THE METER AND ISOLATE THE GAS SUPPLY BY TURNING OFF AT THE METER.**

* Connections may be made in 8mm-dia pipe by a concealed connection from the left hand rear of the appliance with the grommet provided.
* An isolating cock is fitted in the supply feed to the fire to facilitate servicing. It may be rotated for right gas connection.
* When a concealed gas fitting from the rear is required it is necessary to route the pipe to the left side of the unit, taking into account the requirements of BS 6891 1988 dealing with enclosed pipes.
* When installing the firebox into a cavity wall, any part of the installation pipe work installed in the void open to the cavity wall must be enclosed in a gas tight sleeve. It must be sealed at the point at which the sleeved installation pipe enters the fire (The Gas Safety (Installation and Use) Regulations Certificate of exemption number 1 of 1996).Where the pipe enters the fire the outer sleeve must be sealed to the grommet and the pipe must be sealed to its outer sleeve using suitable mastic.


**CHECKING GAS SOUNDNESS**

**\*power must be connected before proceeding with any soundness testing\***

* Complete gas connection to the fire and check for gas soundness in accordance with current codes of practice.

**Power lead routing**

* The power supply for this appliance is provided via AC power adaptor 230 VAC. The main cable terminates at the rear Right hand side of the fire box. The length of the cable provided with the appliance is 1.65 metres. Care must be taken when siting the fire box not to trap the exposed main cable within the builders opening.
* Note: the power cable link to the transformer must be accessible for repairing handset and use with the battery holder
* The cable can be routed using the following two methods,
* Method 1
* Passing the cable through the side of the chimney breast. It is good practice to run the cable within a sleeve of at least 15mm internal diameter, sealing the sleeve using a suitable sealant at the point the sleeve / cable terminates the chimney masonry.
* Method 2
* Remove a channel out of the outer skin of the Dry / wet plaster of the chimney breast up to the main power point. Again it is good practice to run the cable within a sleeve of at least 15mm internal diameter.
* With power points that exceed the 1.65 metre distance, an optional 2.0 metre extension cable is available Part No 7147.
* The cable system consists of retro fitting plug sockets which offers the following options. (Please see figure 5).



# **SECTION TEN Assemble the Appliance (installation instructions)**

* Position the shaped components as described in section four of this manual, it is important that the shapes are positioned exactly as described to ensure the correct operation of the appliance. Badly positioned shapes may result in the gas flame being driven forward onto the glass and permanently marking it.
* Position the glass frame assembly over the top glass frame adjustment bracket so that it locks into place, it may be necessary to adjust the bracket with the 5 castle nuts to obtain a good seal against the glass panel. Ensure that the four studs go through the slots at the bottom of the glass frame.
* Taking great care, tighten the four nuts at the bottom until the glass creates a good seal and adjust the five nuts on the top adjustment bracket if necessary.
* Ensure that the glass compresses the seal on all four sides.
* Locate the 3 holes in the deflector plate, offer them up to the underside of the fire box flange and secure in place with the provided screws.



* Position the fascia so that it is central over the top flange of the combustion box fitting back against the firebox using the magnets provided.

# **SECTION ELEVEN Check Operation of Fire (installation instructions)**

**CHECK BURNER PRESSURE AND GENERAL OPERATION**

* Remove the screw from the pressure test point on the burner inlet elbow and fit a pressure test gauge.
* Turn on the gas to the appliance and operate as described in section three. Check that the inlet pressure 20mbar +/- 1 mbar for natural gas & 37mbar +/-1 mbar for L.P.G.
* Turn off the appliance and remove pressure test gauge.
* Refit the screw into the pressure test point and turn on the appliance again, check that the screw has sealed with leak detection fluid.
* Turn the appliance off.
* Refit the outer fascia.

# **SECTION TWELVE Instruct and Advise the Customer (installation instructions)**

* Demonstrate the lighting and extinguishing procedure to the consumer/user and the removal and refitting of the trim for cleaning.
* Explain that for the first few hours of the fire operating there will be an initial odour. This is due to the curing of the paint, the appliance should be operated on its high setting, and it is recommended that a window is left open until that odour has completely disappeared.
* Instruct on the glass removal and refitting.
* Instruct on the shapes cleaning and advise that a vacuum cleaner can be used but only after all the loose shapes have been removed. ***Refer to ‘Health & Safety Notice (See Section One) at the front of this booklet before proceeding.***
* Advise customer that with use the inside of the air box will change colour, particularly the sides and rear. This is quite normal and often adds to the overall effects of the appliance.
* Advise that the appliance should be serviced annually by a competent person i.e. a **Gas safe registered engineer** in accordance with these instructions.
* Although the appliance is fitted with a glass front which acts as a dress guard it is strongly recommended that a fireguard should be used for the protection of children, the elderly or infirm. Fireguards should conform to B. S. 6539 (1984) (Fireguards for use with solid fuel appliance).
* **Hand these instructions to the user.**

# **SECTION THIRTEEN Maintenance Instructions (maintenance instructions)**

**General**

* Servicing should be carried out annually by a competent person such as a GAS SAFE-registered person in accordance with the relevant regulations, to ensure the safe and correct operation of the appliance.

**Warning: - Before commencing any service or replacement of parts, turn off the gas supply to the fire.**

* After servicing check for gas soundness.
* When ordering spare parts please quote appliance name and serial number these can be found on the data badge, which is located on the left hand side of the base of the appliance.
* If soot has accumulated check to establish cause, rectify and clean flue accordingly.

**Important: - *Refer to ‘Health & Safety Notice (See Page 3) at the front of this booklet before removing the fuel bed components.***

* Examine the shapes for signs of cracking and replace if necessary.(IMPORTANT) see shape layout procedure in section four of this manual before attempting to replace items, which should only be replaced as a complete set with no extra shapes added.

**Replacement of Gas Control**

1. Remove outer trim and turn off the gas supply by the isolation cock.
2. Remove glass panel as described in this manual.
3. Remove all shapes & remove the Burner Bar Edge Cover.
4. Remove the two Burner End Plates (2 = 6 x 3/8 screws in each) and Air Bridge ( 2 x M4 x 10mm screws in each corner).
5. Remove the Black Liners by sliding the two side ones out first, then the rear one should come away forwards.
6. Remove the Stainless Steel Burner by removing the three screws and lift away from the right, being careful not to damage the silencer at the injector and taking note of its position.
7. Disconnect the gas feed supply to the Valve at the valve nut.
8. Disconnect the Valve Motor wire, Ignition wire and Thermocouple interrupter wires from the E.D.B.
9. Remove the 18 screws that hold the burner tray in, and lift out the tray making sure not to damage the Sump Gasket. (If the Gasket is damaged this will require a new one, these can be ordered up through our sales department.)
10. Disconnect all the pipes and thermocouple from the Gas Valve.
11. Change, service or replace the valve and re-assemble in reverse order.
12. Re-assemble the complete tray into the fire in reverse order and re-connect all parts.
13. Turn on the Gas supply, check for soundness and recommission.

**Replacement of Injector**

1. Repeat operations 1-13 for removal of gas control.
2. Clean or replace injector and replace in reverse order, ensuring that the seal around the injector fixing is sound (change if in doubt).
3. Turn on the gas supply, check for soundness and recommission.

**Replacement of the Thermocouple**

1. Remove the Thermocouple from the rear of the Valve.
2. Disconnect the Thermocouple wires from the E.D.B.
3. Undo the Thermocouple nut from the pilot assembly, remove Thermocouple and replace.
4. Replace in reverse order, turn on gas supply, check for soundness, correct operation and recommission.

**Replacement of the Pilot Injector**

1. Repeat operations 1-13 for removal of gas control.
2. Undo the pilot tube nut at the pilot bracket.
3. Pull the pipe gently back taking care not to damage pipe or olive hook nut.
4. Remove the pilot injector from inside the pilot bracket.
5. Clean or replace pilot injector

**Replacement of the EDB Unit**

1. Remove the M3 nuts holding the Heat Shield, remove the M3 nut and remove the E.D.B.
2. Pull the E.D.B. forward and remove all the wires & connections
3. Replace E.D.B. and reconnect all the wires
4. Re-assemble in the reverse order.

Turn on the gas supply, check for gas soundness, operation and re-commission appliance.

**Replacement Handset**

Follow the guide stipulated on page 8 of the users instructions “Changing the handset batteries” to load the batteries into the new handset.

The replacement handset will need to be paired again to the ECU unit.



**Pairing Handset**

* Press eye button to wake handset
* Press &hold star button till menu is displayed –wait for box to fill
* Use wheel to scroll to display – “gas Fire”
* If not paired select – “PAIR”
* While fire is searching disconnect the power lead from the transformer
* Reconnect the transformer (should hear a beep to confirm power reconnected)
* Fire should then be paired

**If the handset not pairing try breaking the power link from the transformer – then get the handset to pairing stage and then reconnect the transformer**


**To delete Pairing**

Press and hold  (approx. 5 seconds) until the menu graphic Completes (see Fig 3). This will access the menu (see Fig 4). Use the selector wheel and select the “gas fire” option. Press  &  simultaneously to delete the current channel. The handset will re-load to “NO DEVICE” see Fig 4) screen.

**When ordering parts quote 'INFINITY 890 BF' and the serial number of the fire, which can be found on the data badge on bottom left hand side of fire. (Refer to cleaning instructions for trim removal.)**

## **SECTION THIRTEEN Wiring Diagram (maintenance instructions)**



Attach to the valve

# BALANCED FLUE GAS FIRE COMMISSIONING CHECKLIST

**This Commissioning Checklist is to be completed in full by the competent person who commissioned the gas fire as a means of demonstrating compliance with the appropriate Building Regulations and then handed to the customer to keep for future reference.**

Failure to install and commission according to the manufacturer’s instructions and complete this Benchmark Commissioning Checklist will invalidate the warranty. This does not affect the customer’s statutory rights. **PLEASE COMPLETE IN BLOCK CAPITALS**.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Customer name: | | | | | | | | | | | | Telephone number: | | | | | | | | | | | | | |
| Address: | | | | | | | | | | | | | | | | | | | | | | | | | |
| Gas Fire make and model: | | | | | | | | | | | | | | | | | | | | | | | | | |
| Installation location: i.e. living/dining room. | | | | | | | | | | | | | | | | | | | | | | | | | |
| Gas Fire serial number: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Commissioned by (PRINT NAME): | | | | | | | | | | | | Gas Safe register number: | | | | | | | | | | | | | |
| Company name: | | | | | | | | | | | | Telephone number: | | | | | | | | | | | | | |
| Company address: | | | | | | | | | | | | | | | | | | | | | | | | | |
|  | | | | | | | | | | | | Commissioning date: | | | | | | | | | | | | | |
| Building Regulations Notification Number (if applicable): | | | | | | | | | | | | | | | | | | | | | | | | | |

|  |  |  |
| --- | --- | --- |
| Site Requirements | Yes | N/A |
| Is the flue terminal sited and fitted as per the manufacturer’s instructions? |  |  |
| Has a flue guard been fitted? |  |  |
| Hearth Requirements- where fitted | | |
| Is the hearth constructed from non -combustible material? |  |  |
| Is the hearth a minimum of 12mm thick with a minimum floor to top surface of 50mm?(BS5871) or as per manufacturer’s instructions? |  |  |
| Is the hearth for open fronted fires a minimum of 760mm wide and has 300mm projecting from the fire opening (BS6871) or to manufacturer’s instructions? |  |  |
| Mounting height (where applicable) has the fire been installed to the correct mounting height- as per manufacturer’s instructions? |  |  |
| Firebox and Fuel Bed | | |
| Has the fuel bed, coals, logs, pebbles etc. been fitted to manufacturer’s instructions? |  |  |
| Gas Supply | | |
| Has an isolation valve inlet elbow been fitted for servicing? | | |
| Has the gas supply been thoroughly purged prior to connection to remove any debris? |  |  |
| Has a gas tightness test been completed prior to breaking into the gas supply and following completion of installation?(IGEM/UP/1B) |  |  |
| Has the correct gas type been chosen as per manufacturer’s instructions? |  |  |
| Record burner gas pressure reading? If only the supply pressure is available a gas rate must be undertaken.(GSIUR REG26/9C) |  | |
| Record dynamic inlet gas pressure (working pressure) reading (all gas appliances running) |  | |
| Installation | | |
| Has the gas fire/convector heater been installed and commissioned in accordance with manufacturer’s instructions? |  |  |
| Has the gas fire/convector heater been installed with the correct clearance to combustible materials, service and general clearances adhered to as per manufacturer’s instructions? |  |  |
| The operation of the fire/convector heater and controls have been demonstrated and understood by the customer, including replacement of batteries? |  |  |
| The manufacturer’s literature, including Benchmark Checklist and Service record has been explained and left with the customer? |  |  |
| Has the appliance been registered with the Local Authority, as detailed on the Gas Safe web site and is a legal requirement and forms part of the warranty? |  |  |
| Commissioning Engineer’s Signature | | |
| Customer’s Signature  (To confirm satisfactory demonstration and receipt of manufacturer’s literature) | | |

\*All installations in England and Wales must be notified to be Local Authority Building Control (LABC) either directly or through a Competent Persons Scheme. A Building Regulations Compliance Certificate will then be issued to the customer

# SERVICE RECORD

**It is essential that your gas fire is serviced regularly and that the appropriate Service Interval Record is completed. Service Provider**

Before completing the appropriate Service Record below, please ensure you have carried out the service as described in the manufacturer’s instructions. Always use the manufacturer’s specified spare part when replacing controls.

|  |  |
| --- | --- |
| **SERVICE 01** | Date: |
| Engineer name: | |
| Company name: | |
| Telephone No: | |
| Gas safe register No: | |
| Comments: | |
|  | |
|  | |
| Signature | |

|  |  |
| --- | --- |
| **SERVICE 02** | Date: |
| Engineer name: | |
| Company name: | |
| Telephone No: | |
| Gas safe register No: | |
| Comments: | |
|  | |
|  | |
| Signature | |

|  |  |
| --- | --- |
| **SERVICE 03** | Date: |
| Engineer name: | |
| Company name: | |
| Telephone No: | |
| Gas safe register No: | |
| Comments: | |
|  | |
|  | |
| Signature | |

|  |  |
| --- | --- |
| **SERVICE 04** | Date: |
| Engineer name: | |
| Company name: | |
| Telephone No: | |
| Gas safe register No: | |
| Comments: | |
|  | |
|  | |
| Signature | |

|  |  |
| --- | --- |
| **SERVICE 05** | Date: |
| Engineer name: | |
| Company name: | |
| Telephone No: | |
| Gas safe register No: | |
| Comments: | |
|  | |
|  | |
| Signature | |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Product ID Label** | | | **A-0390**  **A-0648** | **Serial No Prefix** | | **NE (NG)**  **RF (LPG)** |
| Data Badge | | | | |  | |
| Burner Tray / Box Assembly | | | | |  | |
| Air Test Completed | | | | |  | |
| Battery Insulation Blanket | | | | |  | |
| Warning Label (1409) | | | | |  | |
| Grommet (1406) | | | | |  | |
| Glass Sub-Assembly | | | | |  | |
| Silicone Sealing Strip (4818) | | | | |  | |
| “AAA” Batteries ( 4 ) | | | | |  | |
| Remote Control Hand Set | | | | |  | |
| Transformer (power lead) | | | | |  | |
| Handset Holder (7191) | | | | |  | |
| Battery Holder | | | | |  | |
| Log Set ( Complete ) | | | | |  | |
| Flue/Terminal Kit ( boxed ) | | | | |  | |
| Owners Book | | | | |  | |
| LH/RH Burner End Plates | | | | |  | |
| Air Bridge | | | | |  | |
| Burner Edge Cover | | | | |  | |
| Trim Deflector Plate (6734) | | | | |  | |
| Deflector Plate Instructions and 3 x Black Screws (2056) | | | | |  | |
| Additional Fixings (Part No A-0411) | | | | |  | |
| Nut Spinner | | | | |  | |
| Magnet Rectangles (4) | | | | |  | |
| Inspector |  | | | | | |
| Serial Number | |  | | | | |